## Sheet1
TT | Tên VTTB | Đặc tính kỹ thuật | Đơn vị | Số lượng | Đơn giá | Thành Tiền | HÌnh ảnh | Ghi chú
1 | INVERTER (Loại 10 KVA, điện áp ra 220VAC) | - Loại: G 220 E 230 | Bộ | 2 | 513839734 | 0
- Input voltage: [V] 220
- Input voltage range: [%] - 15 to + 20
- Permitted overlaid AC: [%] < 5 eff.
- AC current feedback on - DC input: [%] < 10 eff.
- Switch on current: < I-Nom.
- Output voltage: [V] 1/N 230 PE
- Adjustment range of output voltage: [%] ± 5
- Voltage tolerance:
+ static ± 1%
+ dynamic ± 4% for 100% load change
-Non-linear load: Crestfaktor ≤ 3
Motor load: 100% permitted (note inrush curre
-Overload behaviour: 50% for 60 sec.
25% for 10 min.
10% for 20 min.
-Short-circuit behaviour: Short circuit proof
-Short circuit current: 3 x I-nom for 3 sec.
- Output frequency: [Hz] 50 (60) ± 0,1% quartz or mains synch
Overload behaviour: 150% for 10 min.
500% for 100 msec.
Transfer time:
- at inverter failure [msec] < 1 (uninterruptible)
- at overload or manual activation [msec] < 1 (uninterruptible)
Synchronisation range: [Hz] 50 (60) ± 3%
Wave form: Sine wave
Distortion factor (acc. EN 62040): ≤ 0,5 with linear load
[%] ≤ 5 with non linear load
Nhà sản xuất:Benning, Đức
2 | Máy tính trạm HP Z840 | HP Z840 Workstation HP Single Unit Packaging HP Z840 1125W (1450W/200V) 90 Percent Efficient Chassis Win 10 Pro 64 Operating System Load to SATA/SAS Intel® Xeon® E5-2650v4 2.2 2400 12C 1st CPU 16GB DDR4-2400 (1x16GB) 1 CPU Registered RAM NVIDIA Quadro M2000 4GB 4xDP 1st No cable included Graphics 512 GB SATA 1st SSD 1 TB 7200 RPM SATA 2nd HDD HP Remote Graphics Software (RGS) for Z HP USB Keyboard & HP USB Optical Mouse 9.5mm Slim SuperMulti DVDRW SATA 1st Optical Disc Drive HP 3/3/3 Warranty SING HP Z840 Country Kit SING HP Dual Processor Air Cooling Kit | Cái | 2 | 0 | 0
3 | Màn hình máy tính | HP Z24n 24-inch Narrow Bezel, IPS Display (ENERGY STAR) | cái | 2 | 14846525 | 14846525
4 | DC isolating transducer | FPD-2, Power: AC 220V, Input: 0-75mV DC, Output1: 4-20mA DC, Output2: 4-20mADC, Class: 0.2% RO | cái | 1 | 8232050 | 0
5 | DC isolating transducer | FPD-1, Power: AC 220V, Input: 0-350V DC, Output: 4-20mA DC, Class: 0.2% RO | cái | 1 | 7596833 | 0
6 | Màn hình LCD tủ rung đảo | Hiệu: BenQ | cái | 1 | 11890517 | 0
Loại: senseye photo
Size: 19''
Tỷ lê: 12,5:14,5
Connector input: VGA Sub-D
7 | Module Diode | Loại:CP DM 10 |  | 5 | 19659512 | 0
Input voltage: 40 VDC max.
Input current:10 A per input max.
Output voltage:Vin - 0.5 typ
Output current:20 A max.
Temperature Operating:-10°C…+55°C (+14°F…+131°F)
-20°C…+85°C (-4°F…+185°F)
Efficiency under max. load:approx. 95.5% at 24 VDC
Mounting rail TS35 to DIN 50022
Horizontal
Clearance: side 2 4 cm; above/below 2
approx. 0.15 kg (0.33 lbs.)
Dimensions (L x W x H):125.0 x 55.5 mm x 110.0 (4.92 x 2.19 x 4.33 in)
Nhà sản xuất:Weidmuller(Đức)
| THÀNH TIỀN TRƯỚC THUẾ |  |  |  |  | 14846525
| VAT (10%) |  |  |  |  | 1484652.5
| THÀNH TIỀN SAU THUẾ |  |  |  |  | 16331177.5